### Praesideo CobraNet™ Interface LBB4404/00

### Architects’ and Engineers’ Specifications

The CobraNet™ interface shall have a network interface for fiber optical hybrid cabling with dual network connections, capable of redundant loop operation. The CobraNet™ interface shall also provide a network interface to an industry-standard Ethernet based CobraNet™ with redundant CAT-5 network connections. The fiber optic network interface of the CobraNet™ Interface shall support multi-channel digital audio and control signals.

The CobraNet™ interface shall transfer up to 4 predefined digital audio channels from the CobraNet™ network to dynamically assigned audio channels on the fiber optic network. Simultaneously, the CobraNet™ interface shall transfer up to 4 dynamically assigned digital audio channels from the fiber optic network to 4 predefined audio channels on the CobraNet™ network.

The CobraNet™ interface shall include sample rate conversion between the audio sample rates of the fiber optic network (44.1 ksps) and CobraNet™ (48 ksps), while conserving volume levels.

The CobraNet™ interface shall be powered from the network for easy installation. The unit shall be able to operate at a maximum operating temperature of 55°C to accommodate high density rack mounting.

The CobraNet™ interface shall have a supervision system to monitor its operation conditions. Network connectivity status and fault conditions shall be displayed on a back-lit LCD on the front panel. In normal operation conditions this LCD will show a configurable name for the CobraNet™ interface to allow for easy identification and a level indicator bar for each input and output. Fault conditions shall also be reported by the unit to a network connected system controller for logging purposes.

The CobraNet™ interface shall have 8 control inputs for activation switches, with configurable supervision for open and short circuits. The control inputs shall have configurable functionality, such as automatically starting an emergency alarm in case of activation by a fire detector or control of background music volume.

The CobraNet™ interface shall have 5 control relay outputs, that can be configured via the network for various functions, such as fault indication or zone activity indication.

The CobraNet™ interface shall be certified by an independent test agency, such as the German TÜV, for compliancy to the standards EN 60849 and EN 54-16 for emergency sound systems.

The CobraNet™ interface cabinet shall be 19”-wide and 2U-high for easy rack mounting without the need for free rack space between units.

The CobraNet™ interface shall be a Praesideo LBB4404/00, manufactured by Bosch Security Systems.